|  | ......................... pcs. .............................. € .............................. € GEZE TZ 300 for securing a door along escape and rescue routes with electrical locking mechanism in accordance with EltVTR. Suitable for connection to a fire alarm system as well as for relaying alarm messages to the building management system; the system comprises: |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € GEZE TZ 300 door control unit With integrated control unit, tested in accordance with EltVTR (German directive for electrical locking systems on escape route doors) Equipment: • Control unit with illuminated emergency push button LED displays for operating states: - Door locked / unlocked / short-term unlocked - Door open / closed - Alarm, pre-alarm, fault Coloured terminals to distinguish connections for the peripherals. Large-surface barrier-free impact cover with sabotage protection. • Integrated emergency push button sign, not illuminated • Key switch with 2 switch contacts incl. Euro profile half cylinder for setting the functions short-time release, permanent unlocking, locking and alarm reset Connections: • 1 input for connecting timer, access control, locks with cylinder contact and much more Function: Short-time release (normally open contact) • 1 input For connecting a fire alarm system, danger alarm system, smoke and heat extraction system Function: Emergency unlocking, after the end of the fire alarm system, danger alarm system, smoke and heat extraction system signal automatic reset of the alarm (normally closed contact) • 1 output for connecting a visual or acoustic alarm indicator and to forward alarm notifications to the building management system function: Alarm (normally closed contact, normally open contact) • Input for illuminated emergency push button sign • Input for feedback of the door status • Input for feedback of the locking state Functions: • Abort and retriggering can be selected in combination with short-term unlocking • Short-time release time 20 seconds • Pre-alarm time 60 seconds • Door alarm when the door is triggered • Integrated buzzer for acoustic signalling during alarms and pre-alarm • Automatic storage of the operating state in the event of power failures • Service mode for suppressing the sabotage alarm Version: ( ) Illumination for the integrated emergency push button sign ( ) Integrated power supply Mains voltage 230 V AC, Operating voltage 24 V DC Output current max. 650 mA (with surface-mounted control units) Output current max. 600 mA (with flush-mounted control units) ( ) Surface-mounted installation: Plastic casing, dimensions (W x H x D): 77x197x90 mm ( ) Colour similar to RAL 6032 (green) ( ) Flush-mounted installation: Switch programme, dimensions (W x H x D): Triple frame 81x223x62.5 mm ( ) AS500 in alpine white by Jung ( ) LS990 in stainless steel by Jung ( ) LS990 in alpine white by Jung ( ) E2 in pure white by Gira ( ) E2 in anthracite by Gira Use for doors: ( ) single leaf ( ) double leaf |
|  | ......................... pcs. .............................. € .............................. € GEZE FTV 320 escape door lock Electric locking mechanism for doors along escape and rescue routes according to the fail-safe principle. Guarantees reliable and immediate unlocking of the door, even with high latch preload. With integrated feedback contact for monitoring the door mode and locking state as well as for sabotage monitoring. High resistance against attempts to break open. Universal application: DIN right / left, horizontal / vertical, door leaf / frame. Face plate pre-mounted to locking element, strike plate can be ordered separately as counterpart. Face plate and strike plate made from corrosion-resistant stainless steel. Operating voltage: 24 V DC, Current consumption: 100 mA in locked state Current consumption: 240 mA briefly during locking Service temperature: -20 / +60 °C Suitability certificate: EltVTR (German directive for electrical locking systems on escape route doors) Resistance against breaking open at least 5,000 N Latch preload: at least 3,000 N Clearance: 5 mm ± 2 mm Dimensions: 15.2 x 138.8 x 37.7 mm (W x H x D) Notes: 1) The escape door lock is installed in addition to the existing panic lock. 2) The face plate version and strike plate version must be specified when awarding the contract/placing the order. |
|  | ......................... pcs. .............................. € .............................. € GEZE MA 500 holding magnet with counterplate for the magnetic locking of emergency exit doors. Resistance against attempts to break open 5,000 N, with integrated Hall sensor for monitoring and bi-colour LED for indicating the door mode. Rated operating voltage 24 V DC, PG9 connection, Current consumption 250 mA, Version: silver-coloured To be installed only using an installation set: ( ) on the hinge side ( ) on the opposite hinge side ( ) for reveal installation with reed contact: ( ) flat reed contact with mounting ( ) flat reed contact with cross hole and mounting base ( ) block reed contact with mounting base for steel doors Note: The holding magnet is usually installed in addition to any panic locks. |
|  | ......................... pcs. .............................. € .............................. € Planning costs Costs for producing cable diagrams and connection diagrams for individual projects and the preparation of functional descriptions. |
|  | ......................... pcs. .............................. € .............................. € Installation, start-up and official approval Installation, start-up and official approval of the system described with instruction. |
|  | ......................... pcs. .............................. € .............................. € Emergency exit system maintenance service package - compact (standard) Service package for maintenance in accordance with EltVTR as well as according to manufacturer’s specifications with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Response time of 24 hours after the fault was reported on workdays (Monday - Friday, 7 am – 5 pm) - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years. |
|  | ......................... pcs. .............................. € .............................. € Emergency exit system maintenance service package - comfort (optional position) Service package for maintenance in accordance with EltVTR as well as according to manufacturer’s specifications with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years. |